Jamaica Broilers Ethanol Dehydration Plant

Wastewater Treatment Facility

Port Esquivel, St. Catherine, Jamaica

Waste Treatment and Disposal Options

Preliminary Analysis

and

Discussion of Effluent Water Quality Standard

Requirement by NEPA/NRCA

Prepared by

FLUID SYSTEMS ENGINEERING LIMITED

OCTOBER 2006

Jamaica Broilers Ethanol Dehydration Plant

Wastewater Treatment Facility

Waste Treatment and Disposal Options

Preliminary Analysis

and

Discussion of Effluent Water Quality Standard

Requirement by NEPA/NRCA

TABLE OF CONTENTS

1.	Introduction	1

2.	Data provided by Jamaica Broilers	2

3.	Summary of waste stream data provided and estimated	5

4.	Sewage Organic and Nutrient Load Estimate	6

4.1.	Discussion of Regulatory Framework	6

5.	Sewage Treatment Options	8

5.1.	Treatment Option Matrix	9

6.	Treatment System Recommendations	10

7.	Stabilization Pond Treatment and its variants	11

8.	Design of Recommended Treatment Facility	11

8.1.	Septic Tank / Anaerobic Pond Option - Description and System capacity	11

8.2.	Septic Tank - Mitigation of operational risks	12

8.3.	Stabilization Ponds - Description and System capacity	13

8.4.	Stabilization Ponds - Operational Risks and Mitigation	16

9.	Location of Proposed Sewage Treatment Ponds	17

TABLE OF FIGURES

Figure 1:  	Topographic Map of Site with Planimetric features	3

Figure 2:  	Oblique aerial photo of site with total project area delineated in red	3

Figure 3:  	Soils within the proposed development site and general vicinity	4

Figure 4:	Aerial view of site and coastal lagoon area	4

Figure 5:	Septic Tank typical detail	12

Figure 6:	General arrangement of the treatment ponds	13

Figure 7:	Location of waste water treatment plant relative to dehydration plant	17

TABLE OF TABLES

Table 1:	 Summary of waste stream data	5

Table 2:	 Composite waste stream projection	6

Table 3:       Untreated Waste Stream Characteristics	6

Table 4:       NEPA Trade Effluent Requirement	7

Table 4:       Treatment Options Matrix	9

Table 5:	 Ponds Design  - Sheet 1	14

Table 6:	 Ponds Design  - Sheet 2	15

Table 7:	 Ponds Design  - Sheet 3	16

# Introduction

The Jamaica Broilers Group, Jamaica’s pioneer commercial producer of broiler meat, has a fully integrated poultry operation and has also diversified into feed milling, cattle rearing, beef production and fish farming, along with the development and marketing of other value-added products for both local consumption and export.

The Jamaica Broilers Group has also devoted significant resources to developing affiliated services that support the varied agricultural operations. These include veterinary and nutritional services, the wholesale and retail of a full range of farm products and the premixing of feed ingredients and concentrate.

The Jamaica Broilers Group recently announced that it would be investing U$14,000,000 to establish an ethanol dehydration plant capable of producing 60 million gallons per year of fuel grade ethanol.

Fluid Systems Engineering Limited, Consulting Engineers was requested to determine the sewage treatment requirement for the waste stream that is expected from this facility. This determination in the first instance is to form the basis of a submission to the National Environmental and Planning Authority NEPA (Jamaica) for a construction permit of the proposed wastewater treatment plant and a license to discharge trade effluent.

Limited information was provided as to the projected quantity and nature of the waste streams for the various components for the dehydration plant. It will therefore only be possible at this stage to prepare outline designs of the treatment options for the expected composite waste stream so that a preferred treatment approach can be selected.

With the selection of the preferred approach, a preliminary design and plant layout will be required for submission to the regulatory agency.

# Data provided by Jamaica Broilers

The following data was provided by the Client. The information is limited and clearly there are implications relating to the operation of the dehydration plant and the source and nature of the hydrous feed stock that will ultimately influence the final waste treatment requirements.

Dehydration Plant

4,000 liters per hour (contains MAX 0.03% alcohol by volume)

{Assume 24/7 Operations}

Typical characteristics are below.

| Sr. No. | Analytical Parameter | Unit | Value |
| --- | --- | --- | --- |
| 1 | Ethanol Content | ppm | 500 max. |
| 2 | Appearance |  | Colourless |
| 3 | BOD | ppm | 150 – 200 |
| 4 | COD | ppm | 300 – 400 |
| 5 | Other Chemicals | ppm | Nil |
| 6 | pH |  | 4 - 5 |

Boiler

Typical blow-down from 40,000 PPH boiler. Will contain Calcium Carbonates and Sulphates.

{Assume 24/7 Operations}

Cooling Tower

Similar characteristics as Boiler – volumes at MAXIMUM of 5,000 liters per hour.

{Assume 24/7 Operations}

Human Wastes

Budget for 50 persons maximum.

The engineers for the dehydration plant provided a preliminary P and ID chart which is attached separately as a PDF file.

Site Location and Key Geographic Features

Figure 1:  	Topographic Map of Site with Planimetric features

The proposed site for the sewage treatment is located on the Portland Bight, a jealously protected coastal zone with rich ecological and natural history features.

Figure 2:  	Oblique aerial photo of site with total project area delineated in red

Figure 3:  	Soils within the proposed development site and general vicinity

Figure 4:	Aerial view of site and coastal lagoon area

# Summary of waste stream data provided and estimated

The following data was provided by the Client or estimated by Fluid Systems where no data was provided.

Table 1:	Summary of waste stream data

Based on the above, the initial estimate of the composite waste stream is set out below.

# Sewage Organic and Nutrient Load Estimate

The untreated waste stream is taken as the weighted composite of the individual contributions i.e.,

Table 2:	Composite waste stream projection

PARAMETER					RAW SEWAGE QUALITY

FLOW						240 m³/day

BOD5						150 mg/l

COD						200 mg/l

TSS						100 mg/l

Total Nitrogen					40 mg/l

Total Phosphates				3 mg/l

Faecal Coliform				1 x 107 MPN/100ml

Table 3:  	Untreated Waste Stream Characteristics

## Discussion of Regulatory Framework

Based on discussions with the NEPA, the proposed treatment plant would normally be required to meet the NRCA’s  Trade Effluent Standards applicable to new plants. This effluent standard requires the following;

PARAMETER					EFFLUENT LIMIT

BOD5						30 mg/l

TSS						50 mg/l

Nitrogen as NO3				10 mg/l

Phosphates as PO4				05 mg/l

COD						100 mg/l

Residual Chlorine 				1.5 mg/l

Faecal Coliform				100 MPN/100ml

Table 4:  	NEPA Trade Effluent Requirement

Based on the above schedules, it will be necessary to remove substantial components of the carbonaceous and nitrogen based pollutants in the raw waste stream.

Disinfection will be necessary for the effluent from the plant to meet the set bacteriological standards.

# Sewage Treatment Options

Generally, the sewage treatment options considered can be classified into four main groups based on the secondary treatment process utilized. For tertiary treatment, common options will be shared. The main groups are;

Suspended Growth Systems:

Activated Sludge

Aeration options: Diffused Air, Surface Aeration, Hybrid

Mixing options: Propeller mixers

BNR: Various proprietary configurations

CNR: Precipitation of phosphates with alum

Disinfection: Chlorine, UV

Sludge Treatment: Aerobic Stabilization, dewatering drying beds.

Activated Sludge (Ditch Systems)

Aeration options: Surface Aeration, Hybrid

Mixing options: Propeller mixers

BNR: Various proprietary configurations

CNR: Precipitation of phosphates with alum

Disinfection: Chlorine, UV

Sludge Treatment: Aerobic Stabilization, dewatering drying beds.

Fixed Growth Systems:

Rotating Biological Contactors

Aeration options: Proprietary entrainment

Mixing options:

BNR: Nitrogen capable only in extended configuration

CNR: Precipitation of phosphates with alum

Disinfection: Chlorine, UV

Sludge Treatment: Aerobic Stabilization, dewatering drying beds.

Hybrid Systems (Fixed and Suspended):

STM-Aerotor™ process.

Aeration options: Proprietary entrainment

Mixing options: Proprietary

BNR: Nitrogen capable, limited Phosphorus

CNR: Precipitation of phosphates with alum

Disinfection: Chlorine, UV

Sludge Treatment: Aerobic Stabilization, dewatering drying beds.

Natural Based Treatment Systems:

Stabilization Ponds, Advanced Ponds Systems, Reed-bed, Rock Filters

Aeration options: Photosynthesis, re-circulation

Mixing options: wind, re-circulation

BNR: Nitrogen capable, Phosphorus (50% ponds, reed-beds, filters)

CNR: N/A

Disinfection: Natural disinfection

Sludge Treatment: Digestion, stabilization integrated

## Treatment Option Matrix

Table 5: 	Treatment Options Matrix

A preliminary analysis of sewage treatment options, considered appropriate for the proposed development suggest that sewage treatment methodologies utilizing low energy input and simple technology for process operation and maintenance should be given the greatest consideration.

Sewage stabilization ponds, configured with anaerobic, facultative, maturation units and recirculation arrangements, presented a robust treatment option. The large land space requirement for the ponds and for the necessary setback in many situations, exclude these solutions.

High rate sewage treatment options based on the activated sludge process, where nutrient removal is available, generally leads to the use of the oxidation ditch process in Jamaica. It provides the best option when energy use and simplicity of operations is considered. The BNR configurations of these systems require increased complexity not appropriate for relatively small sewage flows.

Several proprietary and hybrid high rate suspended and fixed growth treatment systems are available in the marketplace.

Systems with any feature graded un-acceptable will not be considered.

# Treatment System Recommendations

Based on the outcome of the treatment matrix analysis and the general discussion, the following options for sewage treatment for the proposed Jamaica Broilers Ethanol Processing Plant have been reviewed.

- Stabilization Ponds lined (AFM), if a suitable site adjacent to the development area can be found. Land area required 0.3 ha.

- Recirculation enhanced stabilization pond system (AFM³r) with appropriate lining, if a suitable site adjacent to the development area can be found. Land area required 0.22 ha.

# Stabilization Pond Treatment and its variants

Generally for the treatment requirements necessary, a stabilization pond system is highly recommended.

Stabilization ponds wastewater treatment systems have several different configurations.

- The most basic is the use of facultative ponds and maturation ponds (FM³). This configuration also has the highest demand for land.

- By incorporating an anaerobic pond as a pre-treatment system, the land area of the basic system can be reduced by about 15% (AFM³). Odours associated with poorly designed anaerobic ponds have given them a bad ‘rap’ and their use has been generally avoided. Improved design technology has addressed the issues and these systems are now gaining significant acceptance.

- The robust nature of the ponds systems and their wide acceptance has in recent times led to the development of more advanced applications. The (AFM³r) recirculation enhanced pond system is a variant that includes the provision for re-circulation, allowing a high rate of loading of the main treatment pond. This reduces land area requirement but more importantly, gives much needed operational flexibility especially for small systems.

Pond systems are highly integrated biological, physical and chemical ecologic balances. They can get upset and during such times (change of climate, long overcast periods etc.) they do need some help. The (AFM³r) recirculation enhanced pond system is best suited to address such situations.

# Design of Recommended Treatment Facility

## Septic Tank / Anaerobic Pond Option - Description and System capacity

The anaerobic section of the treatment plant will be provided either with the use of a 0.75 day retention septic tank or covered anaerobic lagoon. In the case of a covered lagoon, a de-sludge facility will be provided. The anaerobic section of the plant will allow for the removal of suspended solids and some homogenizing of the waste stream. The sludge load will also be reduced by digestion.  The basic dimensions of the septic tank will be 3m deep x 15m long x 4 m wide.

For the covered anaerobic tank option, the basic dimensions will be 2.5m deep x 16m long x 4.5 m wide adjusted to maintain the prescribed volume within provision of the side slopes.

Figure 5:	Septic Tank typical detail

System fouling due to accumulation of grease and solids - blockage

- The septic tank system is robust and will operate efficiently and without attention for nine to twelve (9 - 12) months. Septic tanks are troubled primarily by hydraulic overload, the disposal of excess grease to the septic tank and the disposal of non-degradable solids. Also, the breakdown of degradable organic solids that are settled out of the sewage by anaerobic digestion can be affected by the disposal of aggressive chemicals in the sewers.

## Septic Tank - Mitigation of operational risks

- Industrial waste septic tanks must be cleaned of accumulated sludge every nine to twelve months or as often as inspections indicate that clearing is necessary.

- The septic tanks should be inspected every three months.

- Large volumes of disinfectant, strong caustic or acidic solutions should not be disposed of in the collection system discharging to the treatment plant.

## Stabilization Ponds - Description and System capacity

The stabilization ponds proposed for secondary treatment of the waste stream is shown below in Figure 6. It will consist of four ponds the first being a facultative pond and the other three maturation ponds. The treatment facility will feature a simple recirculation system that when required, will facilitate the pumping of water from the maturation pond having high levels of dissolved oxygen back to the facultative pond where the main process of oxidation occurs.

Figure 6:	General arrangement of the treatment ponds

The design of the stabilization pond treatment facility is presented in the following three tables.

Table 6:		Ponds Design  - Sheet 1

Table 7:		Ponds Design  - Sheet 2

Table 8:		Ponds Design  - Sheet 3

## Stabilization Ponds - Operational Risks and Mitigation

System distress due to extended period of cloud cover

Pond systems represent highly integrated chemical, biological and physical and ecologic balances. They are known to be robust and can operate successfully without intervention for several weeks. They can get upset from time to time and during such periods (change of climate, long overcast periods etc.) they do need some help.

Risk mitigation

- Risks associated with pond failure due to ecologic imbalances are addressed primarily in the design of the facilities and the monitoring and maintenance provided. During periods of extended cloud cover, it might be necessary to operate the recirculation system. This will ensure that oxygen rich water from the secondary ponds is made available to the primary pond to meet the high oxygen demand related to stabilization of the incoming organic waste.

System distress due to biological upset

Although this tends to occur quite infrequently, ponds do experience biological upset at times.

Risk mitigation

- The recirculation of water from the secondary ponds will re-establish the required biological balance within a period of a day or two and return the system to stability. Odors if they occur at all, will be detectable in the immediate vicinity of the ponds during such period but it must be stressed that such situation are not expected more frequently that once or less per year.

Damage to pond structure due to hurricane storm surge or run-up wave

During the passage of hurricane, high sea water levels associated with storm surge and wave run-up can damage coastal structures.

Risk mitigation

- This risk is addressed primarily in the locating and design of the ponds. The pond embankments will be protected from wave action with the use of a geo-textile cover and stone armour.

# Location of Proposed Sewage Treatment Ponds

Figure 7 below shows the proposed location of the sewage treatment ponds to the south of the dehydration plant.

Figure 7:	Location of waste water treatment plant relative to dehydration plant